## P
Pipe Material (HG BMS, MG BMS, GMS, Cu, Other) | [7 empty] | Hg BMS |  |  | Results
Nominal Pipe Dia (mm) | [7 empty] | 65 |  |  | Velocity (m/s) | [5 empty] | 0.56727
Vol Flow (l/s) | [7 empty] | 2 |  |  | Pr. Drop (Pa/m)/Eq L (m) | [5 empty] | 58.7471 | 2.7346
Percentage Glycol (%) | [7 empty] | 0 |  |  | Specific Heat Capacity | [5 empty] | 4.18
Flow Temperature (deg C) | [7 empty] | 16 |  |  | Calculated Vol Flow (l/s) | [5 empty] | 0
Return Temperature (deg C) | [7 empty] | 19 |  |  | Selection meets CIBSE | [6 empty] | No
Load (kW) | [10 empty] | Criteria
Approximate Sizing Guide
*
10 | 15 | 20 | 25 | 32 | 40 | 50 | 65 | 80 | 100 | 150 | 200 | 250 | 300 | 350 | 400 | 450 | 600
Reynolds Number | [8 empty] | 34681.6466 |  |  | Relative Density | [5 empty] | 0.99844
Kinematic Viscosity | [8 empty] | 1.0959 |  |  | Relative Pipe Roughness | [5 empty] | 0.00068657
Absolute Viscosity | [8 empty] | 1094.1782 |  |  | Internal Pipe Dia (mm) | [5 empty] | 67
Absolute Pipe Roughness (mm) | [8 empty] | 0.046
25.4648 | 11.3177 | 6.3662 | 4.0744 | 2.4868 | 1.5916 | 1.0186 | 0.60272 | 0.39789 | 0.25465 | 0.11318 | 0.063662 | 0.040744 | 0.028294 | 0.020788 | 0.015916 | 0.012575 | 0.0070736
Note on A3: Zemlicka, Pavel: změnit jednotky na kg/h na stránce aplikace, jinak počítat se dá s l/h s tím, že se uvažuje kg=l
Note on J10: Zemlicka, Pavel: Vložit dimenzi 125

## data
DN | 10 | 15 | 20 | 25 | 32 | 40 | 50 | 65 | 80 | 100 | 150 | 200 | 250 | 300 | 350 | 400 | 450 | 600
Internal Bore (mm)
HG BMS | 11.2 | 14.9 | 20.4 | 25.7 | 34.3 | 40.2 | 51.3 | 67 | 79 | 103.3 | 154.3 | 206.5 | 258.8 | 304.8 | 336.6 | 387.4 | 438 | 590
MG BMS | 12.4 | 16.2 | 21.6 | 27.3 | 35.9 | 41.9 | 53 | 68.7 | 80.7 | 105.1 | 155.3 | 208.3 | 260.4 | 309.6 | 339.6 | 390.4 | 438 | 590
GMS | 11.2 | 14.9 | 20.4 | 25.7 | 34.3 | 40.2 | 51.3 | 67 | 79 | 103.3 | 154.3 | 206.5 | 258.8 | 304.8 | 336.6 | 387.4 | 438 | 590
Cu | 10.8 | 13.6 | 20.2 | 26.2 | 32.6 | 39.6 | 51.6 | 64.3 | 73.2 | 105.1 | 155.4 | NA | NA | NA | NA | NA | NA | NA
Other | 10.8 | 13.6 | 20.2 | 26.2 | 32.6 | 39.6 | 51.6 | 64.3 | 73.2 | 105.1 | 155.4 | 206.5 | 258.8 | 304 | 336 | 387 | 438 | 590
Absolute Roughness (mm)
HG BMS | 0.046
MG BMS | 0.046
GMS | 0.15
Cu | 0.0015
Other | 0.02
Pressure Drop (Pa/m) | 4.4247 | Laminar flow |  | Uses Darcy Equ'n for Laminar flow
Flow Factor | -0.061895 | Intermediate flow |  | Calculates Darcy's Coefficient for Intermediate flow
Pressure Drop (Pa/m) | -148.4079 | Intermediate flow |  | Uses Darcy Equ'n for Intermediate flow
Flow Factor | 0.024501 | Turbulent |  | Calculates Darcy's Coefficient for turbulent flow
Pressure Drop (Pa/m) | 58.7471 | Turbulent |  | Uses Darcy Equ'n for Turbulent flow